{"text_format":"2","workbook":"xlsx","n_sheets":1,"sheets":["Лист1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Лист1","index":0,"n_rows":21,"n_cols":10,"rows_kept":21,"cut":false,"hidden":false,"merged":[[2,0,6,0],[7,0,12,0],[13,0,16,0],[19,2,19,5],[20,2,20,5]]}
["Тип","Устройство","Энергопотребление (5В)","Источник питания (5 В)","Источник питания (24 В)","Количество"]
["ЦП","cMT-CTRL01","550mA/2.75w","2А/10 w","210 mA/5.04W",1,{"$f":"J2*F2","v":550},{"$f":"F2*I2","v":5.04},5.04,550]
["Коммуникационные модули","iR-ETN","220mA/1.1 W","2A/10w","100 mA/2.4W",null,{"$f":"J3*F3","v":0},{"$f":"F3*I3","v":0},2.4,220]
[null,"iR-ECAT","270mA/1.35 W","2A/10w","100 mA/2.4W",null,0,{"$f":"F4*I4","v":0},2.4,270]
[null,"iR-COP","170mA/0.85 W","2A/10w","100 mA/2.4W",null,0,0,2.4,170]
[null,"iR-ETN40R","520mA/2.6W","2A/10W","255 mA/6.12W",null,0,0,6.12,520]
[null,"iR-ETN40P","350mA/1.75W","2A/10W","100 mA/2.4W",null,0,0,2.4,350]
["Дискретные каналы","iR-DM16-P","130mA/0.65 W","-","53 mA/1.27W",1,130,1.27,1.27,130]
[null,"iR-DM16-N ","130mA/0.65 W","-","56 mA/1.34W",1,130,1.34,1.34,130]
[null,"iR-DQ08-R ","220mA/1.1 W","-","84 mA/2.02W",1,220,2.02,2.02,220]
[null,"iR-DQ16-N ","205mA/1.02 W","-","78 mA/1.87W",null,0,0,1.87,205]
[null,"iR-DQ16-P ","196mA/0.984 W","-","75 mA/1.8W",null,0,0,1.8,196]
[null,"iR-DI16-K ","83mA/0.418 W","-","31 mA/0.74W",null,0,0,0.74,83]
["Аналоговые каналы","iR-AQ04-VI ","65mA/0.325 W","-","25 mA/0.6W",1,65,0.6,0.6,65]
[null,"iR-AI04-VI ","70mA/0.35 W","-","27 mA/0.65W",null,0,0,0.65,70]
[null,"iR-AM06-VI ","70mA/0.35 W","-","27 mA/0.65W",null,0,0,0.65,70]
[null,"iR-AI04-TR ","65mA/0.325 W","-","25 mA/0.6W",null,0,0,0.6,65]
["Движения","iR-PU01-P ","108mA/0.54 W","-","85 mA/2.04W",null,0,0,2.04,108]
[]
["Потребление источника питания, W",{"$f":"SUM(H2:H18)","v":10.27},"<- Мощность питания 24 В должна быть больше этого значения"]
["Энергопотребление системы, A",{"$f":"SUM(G2:G18)/1000","v":1.095},"<- Не должно превышать 2 А"]